

**REQUEST FOR QUOTATION**

**JOB TITLE: \_\_\_\_\_\_\_\_\_**

**SUPPLIER NAME : ...................................................................................... DUT DATABASE NUMBER: ..................................**

**CO. REG. NO. : ...................................................................... VAT NUMBER : .. .............................................................**

**ADDRESS : ..............................................................................................................................................................................**

**DATE: …………….........................................................**

**The job title must be written on the envelope.**

Suppliers who are interested in supplying the goods as specified hereinafter, and subject to the General and Special conditions of the Durban University of Technology, are requested to complete this set of documents and address it in a sealed envelope marked for **Attention : Procurement and Materials Manager. Envelopes are to be dropped off same in the PROCUREMENT DEPARTMENT, located on the Ground Floor, Block A, M.L. Sultan Campus, 41 / 43 M.L. Sultan Road, Durban, 4001** on the specified Closing time and date. **Please note that no faxed/emailed quotations will be accepted.**

**Site visit details:**

**Date: \_02-05-2018\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Time: 09:00\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_**

**Venue: Alpine Res, Alpine Road \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_**

**Contact person: Lehlohonolo\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Contact number: 031 3732488/ 082 2221551\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_**

I/We hereby quote for the supply of the hereinafter item/s in terms of the SAID description, Specification, Terms and Conditions set herein. The variations are stated where the item offered does not comply with specifications as per original tender.

**RUBBER STAMP**

**........................................... ................................................... ......................................**

**SIGNATURE CAPACITY DATE**

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

 **OFFICIAL USE**

 **DEPARTMENT : PROCUREMENT CLOSED QUOTE NO.**

**CONTACT PERSON : Ernest Dlali Tel: +27 31 37355461**

 **Email:ernestd@dut.ac.za**

**CLOSING DATE : 16-05-2018 CLOSING TIME : 10:00am.**

**Maximum CIDB grading of 4GB will be accepted for building works .**

**All *NEW* service providers are requested to submit the following compulsory documents:**

|  |
| --- |
| The Tax clearance certificate **together with** unique pin must be submitted. Upon evaluation should the service providers tax clearance status printed from the online portal not be in order at close of the RFQ this will lead to the invalidation of the RFQ |
| Certified valid BBBEE certificate (Sanas or IRBA or sworn affidavit) |
| Certified and Valid Entity Registration Documents |
| VAT registration:* Your company must be registered for vat in order to tender
* Vat number must be stipulated on the Original Tax clearance certificate
 |
| Company Profile  |
| Three x letters of references from customers rating your service  |

**OR**

**If you are a current service provider to DUT kindly, provide.**

|  |
| --- |
| **DUT database number**  |
|  |
|  |

**SPECIFICATIONS:**

APLINE RESIDENCE – NEW FIRE HYDRANT SYSTEM

Specification:

* +/- 384mt of 100mm SABS 62 black medium piping
* All necessary steel couplers, elbows, T pieces, sockets for steel piping.
* All necessary welding and flanges made to spec.
* All underground piping to be denzo taped.
* Hiring of all small works equipment for excavation and backfilling.
* Excavate trenches for laying piping.
* Excavation:-

Length: 690m.

Width: 600mm.

Depth: no less than 800mm.

* All excavation must have 75mm river sand bedding and 75mm cover over piping.
* Thrust blocks to be installed where necessary to brace piping.
* Backfilling after testing and mechanically compact at every 200mm intervals to meet existing surface.
* All surfaces excavated must be made good with existing surface (tarred or concreted).
* 1x double booster connection with pressure gauge at entrance of property.
* 1x 50mm ball valve with non-return valve at entrance.
* 12x new brass fire hydrant valves.
* 12x black caps for fire hydrants.
* 12x lockable fire hydrant hose cabinets (to accommodate two hoses).
* 24x 30mt x 65mm Duraflex fire hydrant hoses with couplings.
* 12x AWG jet spray nozzles.
* 9x sets chromadek 290 x 870mm for fire hydrant/hydrant hose/red arrow signage.
* 3x specialised galvanized pole signage with base to accommodate hydrant hose cabinet (made to spec).
* All steel pipe work and fittings are to be S.A.B.S.62 medium grade black.
* All exposed pip work and fittings are to be painted with 1 coat P.A, 10 Primer and 1 coat signal red gloss enamel paint.
* All paintwork is to be touched up after erection.
* All necessary hanging material including unistruts and cantilever arms.
* Usage of jack hammer and scaffolding where necessary.
* All necessary fabrication of piping.
* Transport and delivery of equipment to site.
* Safety file and site establishment.
* Testing and commissioning.